## Info
Description | Example | Format | Allowable ASCII | Comments
Hex Analogue Data | HHHH | Hex | 30-39h + 41-46h | Must contain leading zeros if no data. (0000 to 0FFF)
Hex Digital Data | hhhh | Hex | 30-39h + 41-46h | Must contain leading zeros if no data - least significant bit = first digital
Station Number | NN | Decimal | 30-39h | Number from 0 to 63 (BCD)
BCC Check Sum | YY | Hex | 30-39h + 41-46h | 8 bit addition, carry ignored - example to calculate YY:
strS = "@NNEX_E4:"
lngBCC = 0
For lngN = 2 To Len(strS)
lngBCC = lngBCC + Asc(Mid(strS, lngN, 1))
lngBCC = lngBCC And 255
Next lngN
YY = Hex(lngBCC)
Start Character | @ | Hex | 40h | Ampersand
Termination Character | <CR> | Hex | 0Dh | Carriage Return
Reserved Data | RRRR |  | 30-39h + 41-46h | Not used = 0000
Controller Number | CC | Hex | 30-39h + 41-46h | In decimal multipy the controller no minus 1 by 10, then convert to Hex. = Hex((ControllerNo - 1) x 10)
Space | _ |  | 20h
Analogue Output Number | OO | Decimal | 30-39h | A value from 00 to 07, must have a leading zero = Output Number - 1
Power up read flag | QQ |  |  | Ignore
Digital Count Value | DDDD | Hex | 30-39h + 41-46h | Use an AND to destroy bits 14 & 15 (used by MicroScan only) = &HDDDD AND &H3FFF
Floating point number | ffffffff | IEEE | 30-39h + 41-46h | Must be converted using the IEEE format for 4 byte numbers
byte0 = right most ff (least significant)
byte1 = next right most ff (next least significant)
byte2 = next right most ff (next least significant)
byte3 = left most ff (most significant)
pack the 4 bytes into a 4 byte numeric data type in the same order or use the following function.
Private Declare Sub CopyMemory Lib "kernel32" Alias "RtlMoveMemory" _
(Destination As Any, Source As Any, ByVal Length As Long)
Private Function Convert_Ieee_To_Single(byval strffffffff as String) as Single
Dim bytB(3) As Byte
Dim sngN as Single
If Len(strffffffff) <> 8 Then
Convert_Ieee_To_Single = 0
Else
bytB(0) = CByte("&H" & Right(strffffffff, 2))
bytB(1) = CByte("&H" & Mid(strffffffff, 5, 2))
bytB(2) = CByte("&H" & Mid(strffffffff, 3, 2))
bytB(3) = CByte("&H" & Left(strffffffff, 2))
CopyMemory sngN, bytB(0), 4
Convert_Ieee_To_Single = sngN
End If
End Function
Private Function Convert_Single_To_Ieee(byval sngN as Single) as String
Dim strS As String
Dim bytB(3) As Byte
Dim strIEEE As String
Dim lngN As Long
CopyMemory bytB(0), sngN, 4
strIEEE = ""
For lngN = 0 To 3
strS = Hex(bytB(lngN))
If Len(strS) = 1 Then
strS = "0" & strS
End If
strIEEE = strS & strIEEE
Next lngN
Convert_Single_To_Ieee = strIEEE
End Function
ffffffff resolution formats
Direct Analogue Inputs for mA, V, etc = 0 to 100%
Direct Analogue Inputs for temperature = actual temperature
Controller SV = actual SV
Controller Differential = actual differential

## Com Strings
Stations | Blocks of Data | Send | Receive
2100-D | 12 x DO + 12 X DI - Read | @NNEX_DI:YY<CR> | @NNEX_DI_hhhh_hhhh:YY<CR>
| 12 x DO - Write | @NNEX_DO_hhhh_hhhh:YY<CR> | @NNOK:YY<CR>
| DI 1-4 DI Count Read | @NNRC1:YY<CR> | @NNRC1_QQ_DDDD_DDDD_DDDD_DDDD:YY<CR>
| DI 5-8 DI Count Read | @NNRC2:YY<CR> | @NNRC2_QQ_DDDD_DDDD_DDDD_DDDD:YY<CR>
| DI 9-12 DI Count Read | @NNRC3:YY<CR> | @NNRC3_QQ_DDDD_DDDD_DDDD_DDDD:YY<CR>
2100-A16 | AI 1-4 - Read | @NNEX_E5_00:YY<CR> | @NNEX_E5_00_ffffffff_ffffffff_ffffffff_ffffffff:YY<CR>
| AI 5-8 - Read | @NNEX_E5_01:YY<CR> | @NNEX_E5_01_ffffffff_ffffffff_ffffffff_ffffffff:YY<CR>
| AI 9-12 - Read | @NNEX_E5_02:YY<CR> | @NNEX_E5_02_ffffffff_ffffffff_ffffffff_ffffffff:YY<CR>
| AI 13-16 - Read | @NNEX_E5_03:YY<CR> | @NNEX_E5_03_ffffffff_ffffffff_ffffffff_ffffffff:YY<CR>
| Ambient Sensor (re ffffffff) | @NNEX_E6:YY<CR> | @NNEX_E6_ffffffff_HH_HH_RRRR_HH_RRRR_RRRR_HHHH:YY<CR>
| 2 x DO + 4 x DI + 16 x DO (Relay Board) - Read | @NNEX_DI:YY<CR> | @NNEX_DI_hhhh_hhhh_hhhh:YY<CR>
| 2 x DO + 16 x DO (Remote) - Write | @NNEX_DO_hhhh_hhhh:YY<CR> | @NNOK:YY<CR>
| 4 x DI Count - Read | @NNRC1:YY<CR> | @NNRC1_QQ_DDDD_DDDD_DDDD_DDDD:YY<CR>
| 2 x AO - Read | @NNEX_RO:YY<CR> | @NNEX_RO_HHHH_HHHH_HHHH_HHHH:YY<CR>
| 2 x AO - Write | @NNEX_RO_HHHH_HHHH_HHHH_HHHH:YY<CR> | @NNOK:YY<CR>
| Multiplexer1 - Read (16 Inputs) | @NNEX_E1:YY<CR> | @NNEX_E1_HHH_HHH_…….HHH:YY<CR>
| Multiplexer2 - Read (16 Inputs) | @NNEX_E2:YY<CR> | @NNEX_E2_HHH_HHH_…….HHH:YY<CR>
| Multiplexer3 - Read (16 Inputs) | @NNEX_E3:YY<CR> | @NNEX_E3_HHH_HHH_…….HHH:YY<CR>
| Multiplexer4 - Read (16 Inputs) | @NNEX_E4:YY<CR> | @NNEX_E4_HHH_HHH_…….HHH:YY<CR>
| Controllers1 to 16 - Read | @NNPS_CC:YY<CR> | @NNPS_CC,hhhhffffffffffffffff:YY<CR>
| Controllers1 to 16 - Write | @NNPS_CC,HHHHffffffffffffffff:YY<CR> | @NNPS_CC,hhhhffffffffffffffff:YY<CR>
2100-A4 | AI 1-4 - Read | @NNEX_E5_00:YY<CR> | @NNEX_E5_00_ffffffff_ffffffff_ffffffff_ffffffff:YY<CR>
| Ambient Sensor (re ffffffff) | @NNEX_E6:YY<CR> | @NNEX_E6_ffffffff_HH_HH_RRRR_HH_RRRR_RRRR_HHHH:YY<CR>
| 4 or 8 x DO + 4 x DI + 16 x DO (Relay Board) - Read | @NNEX_DI:YY<CR> | @NNEX_DI_hhhh_hhhh_hhhh:YY<CR>
| 4 or 8 x DO + 16 x DO (Relay Board) - Write | @NNEX_DO_hhhh_hhhh:YY<CR> | @NNOK:YY<CR>
| 4 x DI Count - Read | @NNRC1:YY<CR> | @NNRC1_QQ_DDDD_DDDD_DDDD_DDDD:YY<CR>
| 2 x AO - Read | @NNEX_RO:YY<CR> | @NNEX_RO_HHHH_HHHH_HHHH_HHHH:YY<CR>
| 2 x AO - Write | @NNEX_RO_HHHH_HHHH_HHHH_HHHH:YY<CR> | @NNOK:YY<CR>
| Multiplexer1 - Read (16 Inputs) | @NNEX_E1:YY<CR> | @NNEX_E1_HHH_HHH_…….HHH:YY<CR>
| Multiplexer2 - Read (16 Inputs) | @NNEX_E2:YY<CR> | @NNEX_E2_HHH_HHH_…….HHH:YY<CR>
| Multiplexer3 - Read (16 Inputs) | @NNEX_E3:YY<CR> | @NNEX_E3_HHH_HHH_…….HHH:YY<CR>
| Multiplexer4 - Read (16 Inputs) | @NNEX_E4:YY<CR> | @NNEX_E4_HHH_HHH_…….HHH:YY<CR>
| Controllers1 to 4 - Read | @NNPS_CC:YY<CR> | @NNPS_CC,hhhhffffffffffffffff:YY<CR>
| Controllers1 to 4 - Write | @NNPS_CC,hhhhffffffffffffffff:YY<CR> | @NNPS_CC,hhhhffffffffffffffff:YY<CR>
2100-AO | AO 1 to 4 - Read | @NNEX_RO:YY<CR> | @NNEX_RO_HHHH_HHHH_HHHH_HHHH:YY<CR>
| AO 5 to 8 - Read | @NNEX_R1:YY<CR> | @NNEX_R1_HHHH_HHHH_HHHH_HHHH:YY<CR>
| AO 1 to 4 - Write | @NNEX_RO_HHHH_HHHH_HHHH_HHHH:YY<CR> | @NNOK:YY<CR>
| AO - Write (One output at a time - Outputs 1 to 8) | @NNEX_WA_OO_HHHH:YY<CR> | @NNOK:YY<CR>
| AI 1-4 - Read | @NNEX_E5_00:YY<CR> | @NNEX_E5_00_ffffffff_ffffffff_ffffffff_ffffffff:YY<CR>
| AI 5-8 - Read | @NNEX_E5_01:YY<CR> | @NNEX_E5_01_ffffffff_ffffffff_ffffffff_ffffffff:YY<CR>
| 2 x DO + 12 X DI - Read | @NNEX_DI:YY<CR> | @NNEX_DI_hhhh_hhhh:YY<CR>
| 2 x DO - Write | @NNEX_DO_hhhh_hhhh:YY<CR> | @NNOK:YY<CR>
| DI 9-12 DI Count Read | @NNRC1:YY<CR> | @NNRC1_QQ_DDDD_DDDD_DDDD_DDDD:YY<CR>